## Slide 1: Experimental Physics and Industrial Control System (EPICS)
Dan Crisp
2016-12-15

## Slide 2: Acknowledgments
Some slides in this talk came from
  EPICS Introduction by Andrew Johnson at APS EPICS Training 2014 and at LBNL 2016
  "Accelerator Controls” by Elke Zimoch from PSI at JUAL (Joint Universities Accelerator School) serials
  EPICS Training at PSI by Elke Zimoch from PSI
  Serial training courses by Bob Dalesio
  Overview and Introduction to EPICS from FRIB by Guobao Shen

## Slide 3: Outline
What is an accelerator control system?
What is EPICS?
  EPICS Control System Architecture
  EPICS Channel Access
  EPICS IOC (Input Output Controller)
  EPICS Record
Solve a Problem in EPICS
EPICS Software Toolkit
The EPICS Community

## Slide 4: History of Accelerator Controls
NSLS II, BNL, 2013
Cyclotron, TRIUMF, 1980
RHIC, BNL, 2002
AGS, BNL, 1966

## Slide 5: What is EPICS?
EPICS (Experimental Physics and Industrial Control System)
  a collaboration
  a set of software tools and applications
  a control system architecture
    supports distributed control systems for large research facilities like charged particle accelerators
    distributed software over the network
  use Client/Server methods
  use the Channel Access (CA) network protocol
A collaboration started in 1989 between Los Alamos National Laboratory (GTA) and Argonne National Laboratory (APS)
More than 150 licenses agreements were signed, before EPICS became Open Source in 2004
  http://www.aps.anl.gov/epics/
GTA: Ground Test Accelerator
APS: Advanced Photon Source
Notes: Quote from the EPICS web page (http://www.aps.anl.gov/epics/about.php):
EPICS is a set of software tools and applications which provide a software infrastructure for use in building distributed control systems to operate devices such as Particle Accelerators, Large Experiments and major Telescopes. Such distributed control systems typically comprise tens or even hundreds of computers, networked together to allow communication between them and to provide control and feedback of the various parts of the device from a central control room, or even remotely over the internet.
EPICS uses Client/Server and Publish/Subscribe techniques to communicate between the various computers. Most servers (called Input/Output Controllers or IOCs) perform real-world I/O and local control tasks, and publish this information to clients using the Channel Access (CA) network protocol. CA is specially designed for the kind of high bandwidth, soft real-time networking applications that EPICS is used for, and is one reason why it can be used to build a control system comprising hundreds of computers.

## Slide 6: EPICS Collaboration
EPICS Collaboration

## Slide 7: Who uses EPICS (Very Incomplete List)?
Over 150 independent projects on all continents throughout the science community and US industrial applications

## Slide 8: What can EPICS do?
Typical Distributed Control System Function (DCS) and satisfy technical environment requirements
  Distributed: remote control & monitoring of technical equipment
  Data Acquisition: hardware controls including image data acquisition, data conversions and filtering
  Real time: soft real time process, support real time operating system (VxWorks, RTEMS, et.al.)
  Process control: automatic sequencing of operations, closed loop control like PID controls & feedbacks ( both slow and fast)
  Central services: data trending, archiving, retrieval and plotting
  Security: channel access security
  Time synchronization: time stamps
Others
  Alarm detection, reporting and logging
  Mode and facility configuration control (save/restore)
  Modeling and simulation
  Data analysis

## Slide 9: EPICS Control System Architecture
Network based Client/Server Model (hence the EPICS logo):
For EPICS, client and server refer to their Channel Access role: i.e. Channel Access Client and Channel Access Server
Standard control system architecture, which is often called
  3 tier architecture or 3 layer model
A Server provides information and service
A Client uses the service or asks for the information
EPICS
Client
CA
Client
CA
Server
CA
Server
CA

## Slide 10: What is Channel Access?
A protocol how to transfer data over network
A single data unit is called Process Variable (PV)
  A PV has a unique name, which is used to refer to the data (Naming convention needed!)
A channel is a live connection to a PV
  The detailed operation of Channel Access is unimportant for most programmers (it already works…)
Channel Access is not dependent on a single programming language (native library in C/C++, Java, and C# available)
The entire set of PVs establish a Distributed Real-time Database of machine status, information and control parameters
Process
Variables
CAS
CAS
Process
Variables
CAS
CAS
Process
Variables
CAS
CAS
Process
Variables
CAS
EPICS Database

## Slide 11: How is it Done?
Power Supply
Beam Position Monitor
Vacuum Gauge
Computer Interface
Computer Interface
Computer Interface
Process Variables:
Channel Access Server
S1A:H1:CurrentAO
S1:P1:x
S1:P1:y
S1:G1:vacuum
Channel Access Client
Channel Access Client
Channel Access Client
Network (Channel Access Protocol)
Machine
Operator

## Slide 12: Channel Access Commands
Process Variables:
Channel Access Server
S1A:H1:CurrentAO
S1:P1:x
S1:P1:y
S1:G1:vacuum
Channel Access Client
Who has a PV named “S1A:H1:CurrentAO”?
I do.
What is its value?
25.5 AMPS
Change its value to 30.5
“connection request” or “search request”
OK, it is now 30.5
30.5 is too high. It is now set to the maximum value of 27.5.
You are not authorized to change this value
Notify me when the value changes
It is now 20.5 AMPS
It is now 10.5 AMPS
It is now 0.0023 AMPS
“put” or
“caput”
“get”
or
“caget”
“set a monitor”
“post an event”
or
“post a monitor”
“put complete”
or
or
CA Server
CA Client

## Slide 13: What is an IOC?
IOC means: Input Output Controller
  A special CA Server and CA Client (IOCs can “talk” to each other)
  A computer running the “IOC Core” program (at least once)
  This computer may be:
    VME, cPCI, uTCA, PC laptop, PC workstation, FPGA, ARM
    Running operating system:
      vxWorks, RTEMS, Linux, Windows, OSX, Unix, Soft BLADE
An IOC normally is connected to input and/or output hardware (otherwise called softIOC)
An IOC runs a record database, which defines what this IOC is doing
One IOC != One Computer
  An IOC is one OS process running on a computer
  On single task OS, one IOC == one computer
  An computer could run more than one IOC process
    Linux, Windows, OSX, and so on

## Slide 14: What are Records?
A Record is an object with
  a unique name
  controllable properties (fields)
    contain information (data) different data types can appear in different fields
  A behavior - defined by its record type
  the ability to perform actions on that data
XYZ1234
Employee : James Bond
Badge Number: 007
Address : Whitehall, London
Salary : £70070.07
unique name
fields
data

## Slide 15: Example: View of a Record
field(DRVH,"100")
field(DRVL,"0")
field(HOPR,"80")
field(LOPR,"10")
field(HIHI,"0.0e+00")
field(LOLO,"0.0e+00")
field(HIGH,"0.0e+00")
field(LOW,"0.0e+00")
field(HHSV,"NO_ALARM")
field(LLSV,"NO_ALARM")
field(HSV,"NO_ALARM")
field(LSV,"NO_ALARM")
field(HYST,"0.0e+00")
field(ADEL,"0.0e+00")
field(MDEL,"0.0e+00")
field(SIOL,"")
field(SIML,"")
field(SIMS,"NO_ALARM")
field(IVOA,"Continue normally")
field(IVOV,"0.0e+00")
}
record(ao,"DemandTemp") {
field(DESC,"Temperature")
field(ASG,"")
field(SCAN,"Passive")
field(PINI,"NO")
field(PHAS,"0")
field(EVNT,"0")
field(DTYP,"VMIC 4100")
field(DISV,"1")
field(SDIS,"")
field(DISS,"NO_ALARM")
field(PRIO,"LOW")
field(FLNK,"")
field(OUT,"#C0 S0")
field(OROC,"0.0e+00")
field(DOL,"")
field(OMSL,"supervisory")
field(OIF,"Full")
field(PREC,"1")
field(LINR,"NO CONVERSION")
field(EGUF,"100")
field(EGUL,"0")
field(EGU,"Celcius")
All record fields
have default values
(in case they are not specified by the developer)

## Slide 16: Example Record
Temperature Sensor
IOC
Database
Analog to Digital Converter
0 – 100°C
0 – 10V
8 bit ADC
0 – 10V
0 – 255 bits
Process
Normal Operation
5 - 50°C
record (ai, “MTRT1-TEMP:READ”)
{
field (EGU, “deg C”)
field (EGUL, “0”)
field (EGUF, “100”)
field (HSV, “MAJOR”)
field (HIGH, “51”)
field (SCAN, “.1 second”)
field (DTYP, “Hy8401”)
field (INP, “#C3 S0 @”)
}

## Slide 17: Solve a Problem in EPICS
Problem:
In the LINAC we have a water chiller that must be turned ON whenever the average temperature of two temperature sensors rises above a set point. The set point is nominally 10 degrees centigrade.
Binary out
MTRT1-LI-COOL:SW
Calculation
MTRT1-LI-COOL:CALC
CALC: ( (A+B)/2 ) > C
C: 10
SCAN: 10 second
Analog In
MTTR1-LI-COOL:TEMP1
EGU: deg C
VAL
INP
EGU: deg C
VAL
INP
INPB
INPA
VAL
DOL
OUT
T2
Sensor
Sensor
T1
IOC
Database
ADC
ADC
Binary I/O
Chiller
Analog In
MTRT1-LI-COOL:TEMP2

## Slide 18: EPICS CLI Tools
Read a PV named <NAME>
caget NAME
Get information
cainfo NAME
Start a monitor
camonitor NAME
(Cancel with [Ctrl] + [c])
Without argument all commands show some help
Set value to a PV
caput NAME VALUE
caget MTRT1-TEMP:READ
cainfo MTRT1-TEMP:READ
camonitor MTRT1-TEMP:READ
caget
caput DemandTemp 24.0

## Slide 19: EPICS Software Toolkit
“Installing EPICS” does not create a control system
The EPICS Software Toolkit consists of hundreds of pieces of software
  Some are individual programs for performing specific tasks
    Creating and running Graphical User-Interfaces, archiving data, monitoring alarms etc.
  Others are code libraries for monitor or control of specific kinds of hardware
    IOC device and driver support for COTS equipment (PLCs, oscilloscopes etc.)
  Others allow common programming languages and tools to interface with EPICS
    C/C++, Perl, Python, Java, Matlab/Octave, C#, LabView etc.
  Almost all EPICS code is Open Source (freely usable & modifiable)
    EPICS Open License is BSD-like; the GNU GPL and LGPL are also used
An EPICS control system can be made by choosing and configuring existing software
  Writing code is often only necessary to fill gaps in the available tools

## Slide 20
Leadership is mostly informal
  Bob Dalesio, runs Osprey DCS (EPICS Consultancy)
    Original author of GTACS and EPICS
    Community development
    Organizes collaboration meetings
  Andrew Johnson, Computer Scientist at APS, Argonne
    Manages website, mailing lists etc.
    Maintenance lead for EPICS Base (V3)
3 public mailing lists
  tech-talk is the main user list
  core-talk is for core developers
  pvdata-devel is for V4 developers
Open to anyone
  tech-talk has 800 subscribers
Questions asked at all levels
  Members are usually very helpful
Posts from non-members are moderated to discourage spam
  High signal/noise ratio
GNU Mailman handles subscriptions, moderation, daily digest
Searchable archives back to 1994
  RSS Feeds of messages
Leadership is mostly informal
  Bob Dalesio, runs Osprey DCS (EPICS Consultancy)
  Andrew Johnson, Computer Scientist at APS, Argonne

## Slide 21: EPICS Resources
Central site for EPICS
  http://www.aps.anl.gov/epics/
  Documentations
    CA Clients
    Device support (driver)
    Tech-talk (mailing list and archive)
Useful links for trainings
  http://www.aps.anl.gov/epics/docs/training.php
  http://www.aps.anl.gov/epics/docs/GSWE.php
  http://epics.web.psi.ch/training/downloads

## Slide 22: EPICS Process Database
Process Block execution time varies from block type to block type
AI on a PowerPC ~100,000/second (50% idle)
AI on a 68060 is ~18,000/second (50% idle)
Fastest periodic scan rate is dependent on OS clock tick – 1 KHz
Interrupt scanning is limited by the CPU bandwidth (interrupt delay ~15usec)
Name resolution - 100,000/second - runs at the lowest priority
Support to particular physical I/O is distinct from process logic - ASCII device type
The numbers are just example with extremely old CPU, and probably no longer meaningful to a modern computer.

## Slide 23: Backup

## Slide 24: Record Processing
Record processing can be periodic or event driven:
Periodic: Standard scan rates are…
  10, 5, 2, 1, 0.5, 0.2 and 0.1 seconds
  Custom scan rates can be configured up to speeds allowed by operating system and hardware
  No precise timing!
Event driven: Events include
  Hardware interrupts
  Request from another record via links
  EPICS Events
  Channel Access Puts
Record Processing means:
Trigger Record to do what it is configured to do.

## Slide 25: Solve a Problem in EPICS
The major software components of an IOC (IOC Core)
Inside an IOC
Sequencer
LAN (Network)
Device Support/Device Driver
I/O Hardware
IOC
Process Database
Channel Access

## Slide 26: EPICS Process Database
A collection of EPICS record(s)
Process Blocks are the basic elements: AI, AO, BI, BO, Motor, CALC, PID, SUB, etc.…
Process Blocks consist of fields for: SCHEDULE, I/O, CONVERT, ALARM, MONITOR
They hold runtime values: VALUE, TIMESTAMP, ALARM CONDITION, etc.…
New process block are easily added
Configured using Text Editor or some EPICS tools like VDCT, GDCT
Loaded as ASCII records at boot time
All fields can be read/written through the channel access client interface during operation
ca-server
Process DB
Device support
ca-client
LAN
Driver support
Device Driver

## Slide 27: Community Organization
Leadership is mostly informal
  Bob Dalesio, runs Osprey DCS (EPICS Consultancy)
    Original author of GTACS and EPICS
    Community development
    Organizes collaboration meetings
  Andrew Johnson, Computer Scientist at APS, Argonne
    Manages website, mailing lists etc.
    Maintenance lead for EPICS Base (V3)
Various development groups exist and have their own leadership
  EPICS Core Developers (Andrew Johnson)
  EPICS V4 Working Group (Bob Dalesio and Andrew Johnson)
  Control System Studio (Eric Berryman, FRIB at MSU)
  Distributed Information Services for Control Systems (Dylan Maxwell, FRIB at MSU)
  AreaDetector (Mark Rivers, Uchicago)
Occasional meetings of management of the main labs to discuss effort & direction

## Slide 28: Mailing Lists
3 public mailing lists
  tech-talk is the main user list
  core-talk is for core developers
  pvdata-devel is for V4 developers
Open to anyone
  tech-talk has 800 subscribers
Questions asked at all levels
  Members are usually very helpful
Posts from non-members are moderated to discourage spam
  High signal/noise ratio
GNU Mailman handles subscriptions, moderation, daily digest
Searchable archives back to 1994
  RSS Feeds of messages

## Slide 29: What is an Accelerator Control System?
A computer environment to solve simultaneously requirements of different user groups to run an accelerator
Connect the Operator in the control room with the accelerator hardware. The control room might not be near the accelerator
Operator in Control Room
Control System
Notes: The Accelerator Control System connects the Operator in the control room with the accelerator hardware. The control room might not be near the accelerator:
-SLS is 200m away from PSI main control room -For SwissFEL the control room will be a kilometer away -Some experiments are controlled remote from all over the world

## Slide 30: What is an Accelerator Control System? Technical Environment
Control Systems (one way or another) have to deal with …
Distributed end points and processes
  Geographically over for example miles
  Hundreds of thousands of signals, millions of process variables
Data Acquisition (front end hardware)
Real-time needs (where necessary)
Process control (automation, feedback, PID controller)
Central Services (Archive, Databases, Name Resolution)
Data transport (control system protocol, network)
Security (who’s allowed to do what from where?)
Time synchronization (time stamps, cycle ids, etc.)
that is: Computers (in different flavors) and Computer Environment

## Slide 31: History of Accelerator Controls
Prof Donald Kerst with the first betatron invented in 1940 at the University of Illinois
Diagnostics
Settings
Accelerator Control System
Notes: No Control System needed because:
-Direct tuning with knobs -Direct diagnostics with own eyes -(Very) limited number of devices involved
-> so the brain is the Accelerator Control System in this case

## Slide 32: Solutions: Different Control System Examples
System Name:
EPICS
TANGO
DOOCS
ACS
SCADA (PVSS)
Pro:
Bugs are already found
Cons:
Learning curve to adapt
to your problems
Pro:
Your problems solved
perfectly
Cons :
You are on your own
(no one can help)
Pro:
Outsource your problems
Cons :
Expensive
Collaborations:
Used at more than one Lab
Single Site Systems:
Developed and used in one Lab
Commercial System
Notes: SCADA = Supervisory control and data acquisition
Best solution: all systems are used somewhere to control accelerators successful.
All systems support good experiments and produce excellent science.
Therefore, the choice of system is political not technical.

## Slide 33: EPICS Supports Standard Control System Model
OS:
Unix/Linux
Windows
I/O Controllers:
VME,VXI
PCI, PCIe, uTCA, PLC,
Softcores on FPGAs
OS:
vxWorks, Unix, Windows
RTEMS, RTLinux, Linux
Instruments
Remote and Local I/O Buses:
Control Net, PCI, CAN-Bus, Industry Pack, VME, VXI, PCI, ISA, CAMAC, GPIB, Profibus, Bitbus, Serial, Modbus, Yokogawa, G-3, Ethernet/IP, RS232,
Many more….
Site LAN/WAN
Instruments
Instruments
Notes: Three-tier standard model for distributed control systems.
The hardware layer was considered dumb when the terminology was developed.
Meanwhile “hardware” can be as complicated as a robot (with its own controller) or an oscilloscope (with an operating system installed on a specialized computer).
More and more logic is moved to the hardware layer.

## Slide 34: Channel Access Network Flow
CA Client
CA Server 1
CA Server 2
CA Server 3
Network
1. Query: Broadcast
2. Answer: direct connection
3. All further queries and answers work directly (Point-To-Point)

## Slide 35: Parts of EPICS
Output
Input
CA Server
IOC
Control Room
CA Client
CA Client
CA Server
Server Programs:
(user programs)
Realtime Control
Records
Client Programs:
Alarm, Striptool, CS-Studio,
many more …
(user programs)
Channel Access:
(UDP/TCP)
Hardware: maybe
controllers and PLCs

## Slide 36: Close Look at a Measured Value
295.5
with a unit mA
with a time stamp 17.2.2005 14:21:16
with a severity (alarm state) NO_ALARM
with technical limits 0 to 400
with graphical limits 0 to 370
A measured value is an object with multiple related information
that have different data types.
One object is called an EPICS record
with a description "Beam current in SR"
Value with a data type

## Slide 37: Make a Record from a Measured Value
Configured by developer
VAL
SEVR
TIME
295.5
with a unit mA
17.2.2005 14:21:16
NO_ALARM
with technical limits 0 to 400
with graphical limits 0 to 370
with a description "Beam current in SR"
A value with a data type
with a unique name ARIDI-PCT:CURRENT
ai
record (ai, "ARIDI-PCT:CURRENT") {
with a time stamp
Read back from hardware/driver
with a severity (alarm status)
field (EGU, "mA")
field (EGUF, "400")
field (EGUL, "0")
field (HOPR, "370")
field (LOPR, "0")
field (DESC, "Beam current in SR")
field (DTYP, "HY8401")
field (INP, "#C3 S0 @")
}

## Slide 38: Process Variable (PV)
A PV name is comprised of two parts
  The record name, and
  the name of a field belonging to that record
For example…
Note that if no field name is given, Channel Access will default to using the .VAL field “ARIDI-PCT:CURRENT” is interpreted as “ARIDI-PCT:CURRENT.VAL”
As well as a value, a PV has other attributes, e.g.
  Engineering units string, Timestamp, Alarm status and severity
  Operating range (Low .. High)
  Control limits (Low .. High)
A record name
ARIDI-PCT:CURRENT
A field name
EGU
.
A dot to join them
A Process variable name
that means: most record fields can be accessed individually

## Slide 39: What do Records do?
Analog in
Analog out
Binary in
Binary out
Calculation
Calculation out
Compression
Data fanout
Event
Fanout
Histogram
Motor
Multi bit binary input
Multi bit binary output
PID control
Pulse counter
Pulse delay
Scan
Select
Sequence
String in
String out
Subarray
Subroutine
Waveform
Depends on
  Record Type
  Field values
Records are active, they do things
  Get data from other records or from hardware
  Perform calculations
  Check values are in range and raise alarms
  Put data to other records or to hardware
  Activate or disable other records
  Wait for hardware signals (interrupts)
record do nothing until they are processed
incomplete
list!

## Slide 40: Example Record
Value (34 °C)
CA Client: CS-Studio
Driver
Device Support
Record Support
record (ai, “MTRT1-TEMP:READ”)
{ …
field (SCAN, “.1 second”)
field (DTYP, “Hy8401”)
field (INP, “#C3 S0 @”)
field (VAL, “34”)
… }
every 0.1 seconds the record asks the driver for a value
and the driver reports back
CS-Studio sets a CA monitor
every time the value changes record triggers callback
IOC

## Slide 41: EPICS Software Toolkit
Network Attached Devices
IOC
IOC
IOC
Network Protocols Channel Access pvAccess
IOC Software
PV Database State Programs StreamDevice asynDriver synapps areaDetector mca motor sscan caputRecorder softGlue modbus autosave
Client Programs
CS-Studio BOY Archive Appliance BEAST Python Olog
Server Applications
CA Gateway pcaspy
Custom Chassis/Panels
Technical Equipment
Commercial Instruments
IOC
CAS
pvaSrv

## Slide 42: Another View of EPICS Architecture
Channel Access Client (CAC)
Connection Data Transfers
WAN/LAN/Local
Connection Data Transfers
Channel Access Server (CAS)
DB Engine
Device Support
Driver Support
I/O Controller
Archiving
Archive Access
Archive Viewing
Archive Analysis
Types
Connection Server
Program Interfaces
C, C++, Fortran, JAVA
IDL / Matlab / Mathematica
ActiveX / DDE / VisBasic
SDDS / SAD /
tcl / PERL / Python
State Notation Lang / FSQT
Integrate other systems
Like Labview or legacy
systems
User Tools
DM/MEDM/DM2K/EDM/JDM
Control System studio,
Alarm Handler / stripTool/
knobManager
Physics Toolkits
Experiment Toolkits
EPICS Process Database

## Slide 43: 10 Really Neat Things About EPICS
It is free
It is Open Source
There are lots of users
All a client needs to know to access data is a PV name
You can pick the best tools out there …
… or build your own
The boring stuff is already done
There is a lot of expertise available close by
A good contribution becomes internationally known
It does not matter, if you need 10 or 10 million PVs
It is fun

## Slide 44: Review of EPICS Terminology
EPICS: a collaboration, a set of software tools and applications, and a control system architecture
Channel Access: a protocol to transfer data over network
IOC: Input Output Controller, one IOC != one computer
Record: an object with a unique name and various fields
Process database: collection of record(s)
PV: process variable, one PV == oneRecordName.field, field by default is VAL
Channel: a live connection to a PV